## Server_Protocol
Data From Device To Server
Byte No. | No. of Bytes | Data Type | Data Format | Parameter | Data Sample | Comment
0-4 | 5 | UINT8 | ASCII | Server Identification | LGURU
5 | 1 | UINT8 | DECIMAL | No. of Bytes to be Transmite | 65
6 | 1 | UINT8 | DECIMAL | Packet Identification 0x01 - DG OFF 0x02 - DG ON 0x03 - EB OFF 0x04 - EB ON 0x05 - Accelerometer Interrupt 0x06 - GPS Position Changed 0x07 - Fuel Filling Just Finished 0x08 - External Battery Connected 0x09 - External Battery Disconnected 0x10 - Scheduled Packet | 0x09 | Need to convert Decimal to Hex at server side.
7-10 | 4 | UINT8 | ASCII | Hardware Version | 1.01
11-14 | 4 | UINT8 | ASCII | Software Version | 1.00
15-29 | 15 | UINT8 | ASCII | IMEI | 861359032489146
30-33 | 4 | UNIT8 | ASCII | Sim Operator (First Four Char) | Voda
34 | 1 | UINT8 | DECIMAL | Signal Strength | 31
35-38 | 4 | FLOAT32 | DECIMAL | GPS Latitude | 28.37087 | Need to convert in float at server side.
39 | 1 | UINT8 | ASCII | North/South | N
40-43 | 4 | FLOAT32 | DECIMAL | GPS Longitude | 76.88411 | Need to convert in float at server side.
44 | 1 | UINT8 | ASCII | East/West | E
45-48 | 4 | FLOAT32 | DECIMAL | Fuel Filled Quanity (in liter) | 30.53 | Need to convert in float at server side.
49 | 1 | UINT8 (BCD) | DECIMAL | Year | 18
50 | 1 | UINT8 (BCD) | DECIMAL | Month | 07
51 | 1 | UINT8 (BCD) | DECIMAL | Date | 16
52 | 1 | UINT8 (BCD) | DECIMAL | Hours | 12
53 | 1 | UINT8 (BCD) | DECIMAL | Minutes | 16
54 | 1 | UINT8 (BCD) | DECIMAL | Seconds | 53
55 | 1 | UINT8 | BIT0 | DG ON/OFF (1: ON, 0: OFF) | 1 | Need to convert in Bits and then process at server side.
|  |  | BIT1 | EB ON/OFF (1: ON, 0: OFF) | 1
|  |  | BIT2 | Supply from External Batt (1: YES, 0: NO) | 1
|  |  | BIT3 | Accelerometer Status (1: Tempered, 0: Normal) | 1
|  |  | BIT4 | FUTURE USE | 0
|  |  | BIT5 | FUTURE USE | 0
|  |  | BIT6 | FUTURE USE | 0
|  |  | BIT7 | FUTURE USE | 0
56 | 1 | UINT8 | DECIMAL | FUTURE USE | 0
57 | 1 | UINT8 | DECIMAL | FUTURE USE | 0
58 | 1 | UINT8 | DECIMAL | FUTURE USE | 0
59 | 1 | UINT8 | DECIMAL | FUTURE USE | 0
60 | 1 | UINT8 | DECIMAL | FUTURE USE | 0
61 | 1 | UINT8 | DECIMAL | FUTURE USE | 0
62 | 1 | UINT8 | DECIMAL | FUTURE USE | 0
63-64 | 2 | UINT16 | DECIMAL | CRC | 10256
Server ACK
Byte No. | No. of Bytes | Data Type | Data Format | Parameter | Data Sample
0 | 1 | UINT8 | DECIMAL | Packet Identification 0x01 - DG OFF 0x02 - DG ON 0x03 - EB OFF 0x04 - EB ON 0x05 - Accelerometer Interrupt 0x06 - GPS Position Changed 0x07 - Fuel Filling Just Finished 0x08 - External Battery Connected 0x09 - External Battery Disconnected 0x10 - Scheduled Packet | 0x09
1-3 | 3 | UINT8 | ASCII | ACK (Acknoledge: ACK, Error: ERR) | ACK
4 | 1 | UINT8 (BCD) | DECIMAL | Year | 18
5 | 1 | UINT8 (BCD) | DECIMAL | Month | 07
6 | 1 | UINT8 (BCD) | DECIMAL | Date | 16
7 | 1 | UINT8 (BCD) | DECIMAL | Hours (24 hours format) | 12
8 | 1 | UINT8 (BCD) | DECIMAL | Minutes | 16
9 | 1 | UINT8 (BCD) | DECIMAL | Seconds | 53
10-11 | 2 | UINT16 | DECIMAL | CRC | 10256

## SMS_Format
SMS DATA FORMAT
Byte No. | No. of Bytes | Data Type | Data Format | Parameter | Data Sample
0-4 | 5 | UINT8 | ASCII | Server Identification | LGURU
5-6 | 2 | UINT8 | DECIMAL | No. of Bytes to be Transmite | 65
7-8 | 2 | UINT8 | DECIMAL | Packet Identification 0x01 - DG OFF 0x02 - DG ON 0x03 - EB OFF 0x04 - EB ON 0x05 - Accelerometer Interrupt 0x06 - GPS Position Changed 0x07 - Fuel Filling Just Finished 0x08 - External Battery Connected 0x09 - External Battery Disconnected 0x10 - Scheduled Packet | 09
9-12 | 4 | UINT8 | ASCII | Hardware Version | 1.01
13-16 | 4 | UINT8 | ASCII | Software Version | 1.00
17-31 | 15 | UINT8 | ASCII | IMEI | 861359032489146
32-35 | 4 | UNIT8 | ASCII | Sim Operator (First Four Char) | Voda
36-37 | 2 | UINT8 | DECIMAL | Signal Strength | 31
38-45 | 8 | FLOAT32 | DECIMAL | GPS Latitude | 28.37087
46 | 1 | UINT8 | ASCII | North/South | N
47-54 | 8 | FLOAT32 | DECIMAL | GPS Longitude | 76.88411
55 | 1 | UINT8 | ASCII | East/West | E
56-61 | 6 | FLOAT32 | DECIMAL | Fuel Filled Quanity (in liter) | 030.53
62-63 | 2 | UINT8 (BCD) | DECIMAL | Year | 18
64-65 | 2 | UINT8 (BCD) | DECIMAL | Month | 07
66-67 | 2 | UINT8 (BCD) | DECIMAL | Date | 16
68-69 | 2 | UINT8 (BCD) | DECIMAL | Hours | 12
70-71 | 2 | UINT8 (BCD) | DECIMAL | Minutes | 16
72-73 | 2 | UINT8 (BCD) | DECIMAL | Seconds | 53
74 | 1 | UINT8 | BIT | DG ON/OFF (1: ON, 0: OFF) | 1
75 | 1 | UINT8 | BIT | EB ON/OFF (1: ON, 0: OFF) | 1
76 | 1 | UINT8 | BIT | Supply from External Batt (1: YES, 0: NO) | 1
77 | 1 | UINT8 | BIT | Accelerometer Status (1: Tempered, 0: Normal) | 1
78-82 | 5 | UINT16 | DECIMAL | CRC | 10256